## Sheet1
S.NO. | DISTRIBUTION PANEL | UNIT | QNTY
1 | Supply,Receiving Unloading, handling at site, storing, installation in correct assigned positions at , effecting proper connections, testing & commissioning shifting, fixing ,including & supervision during installation, testing and commissioning of 2 mm thick MS sheet steel fabricated cubicle type Panel dust and vermin proof complete with hinged and lockable doors .The Sheet Steel shall under go minimum eight tank treatment followed by finishing treatment of powder coating with 70 micron minimum thickness. All the panels shall be floor mounted and dead front construction complete with interconnections. & Same panel shall be fixed on exesting foundations. The distribution board enclosure shall be made of electro-galvanized steel sheet (minimum thickness 2 mm for load bearing members and 1.6 mm thick for other members) and finished with epoxy-powder coating (minimum 60 micron) colored to the Engineer’s acceptance. The enclosure shall be completed with hinged doors and to be provided with standardized key lock and 3 sets of keys shall be provided for each distribution board
Note:-
a) | The panels shall be FRONT operated, with cable entry from the bottam Earth bus shall be part of the panel.) (All MCB to be "C" Curve)
b) | The following provisions shall be required to be made in the Distribution Panel as detailed below:
i) | All live accessible parts shall be shrouded with 1mm thick polycarbonate/3 mm thick FRP sheet and all equipment shall be finger touch proof. The busbar insulation shall be with heat shrinkable sleeves according to the colour code. SMC shrouds and busbar supports shall be used. All MCCB door handle shall be interlocked and lockable in OFF position.
ii) | Galvanised hardware with zinc passivation shall be used in fabrication of Switchboards.
iii) | Suitable Aluminium earth bus to be provided throughout the length of Switchboards.
iv) | All indication lamps / illuminated push buttons shall be LED type.
v) | Coil of all motor starters shall be fed from 440 V / 230 V Control Transformer.
vi) | 2A SP MCBs shall be used as backup protections.
vii) | All MCCBs shall be variable plug setting type with thermal magnetic up to 630 A rating and with microprocessor based releases above 630 A rating, line load reversibility, Ics = 100% Icu,& rotary handle.
viii) | All control& power wiring shall be broughtout upto the cable alley in the terminal blocks.
ix) | An approval shall be taken for each panel before manufacturing.
x) | Provision of one 6/16 amp socket & compartment lighting for each vertical section of main panel.
xi) | Illuminated push button on Starter Panels of Pumps.
aa) | Interlocking / Auto start command terminals for starter Panels.
ab) | All breaking Capacity for ACB to be Ics=100%Icu and Icw for 1 sec..
ac) | All breaking Capacity for MCCB to be Ics=100%Icu.
ad) | All MCB to be C Curve
Space heater shall be provided with thermostat with suitable size DP MCB as backup protection suitable location in all feeder pillars
A | AC PANEL
Incoming:
1 no. of 315 Amp FP MCCB of 26KA breaking capacity.
Metering for incoming:
Digital Multifunction meter with RS-485 communication port for measurement of PF, V, A & Hz , equivalent to EM6459,with CT as required.
Phase indicating lamps RYB with 2 Amps SP MCB back up.
ON / OFF indicating lamps
Bus Bars:
Electrolytic high conductivity Aluminium three phase and neutral busbars rated at 400 Amps, insulated with heat shrinkable coloured PVC sleeves & clip on shrouds for joints. Current density of Bus Bar to be 1.3 sq.mm / amp.
Outgoing (All MCB/MCCB shall be suitable for motor duty):
i) | 5 Nos. 100 amp FP MCCB of 10 KA breaking capacity for 22HP & 32HP
2 Nos. 63 amp FP MCB of 10 KA breaking capacity for 14HP
4 Nos. 40 amp FP MCB of 10 KA breaking capacity with Dol starter for terrace lift pressurization
5 Nos. 40 amp FP MCB of 10 KA breaking capacity 5HP
| AC PANEL as described above shall be complete with all interconnections, risers, internal wiring, labels, terminal blocks etc. complete as required. | SET | 1